{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":30,"n_cols":7,"rows_kept":30,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FTXJ-MS / RXJ-A"]
[]
[]
[]
[]
["","","","","FTXJ25MV1BS / RXJ25A5V1B","FTXJ35MV1BS / RXJ35A5V1B","FTXJ50MV1BS / RXJ50A2V1B"]
["Cooling capacity","Min.","","kW","","","1.40"]
["","Nom.","","kW","2.40","3.50","4.80"]
["","Max.","","kW","","","5.50"]
["Heating capacity","Min.","","kW","","","1.10"]
["","Nom.","","kW","3.20","4.00","5.80"]
["","Max.","","kW","","","7.00"]
["Nominal efficiency","Annual energy consumption","","kWh","254","428"]
["","COP","","","4.57","4.04","3.65"]
["","EER","","","4.73","4.09","3.35"]
["","Energy labeling Directive","Cooling","","A","A","A"]
["","","Heating","","A","A","A"]
["Space cooling","Annual energy consumption","","kWh/a","97","170","239"]
["","Energy efficiency class","","","A+++","A++","A++"]
["","Capacity","Pdesign","kW","2.40","3.50","4.80"]
["","SEER","","","8.64","7.19","7.02"]
["Space heating (Average climate)","Annual energy consumption","","kWh/a","822","913","1,505"]
["","Capacity","Pdesign","kW","2.70","3.00","4.60"]
["","Energy efficiency class","","","A++","A++","A+"]
["","Pdh Heating capacity at -10°","","kW","2.18","2.61","4.16"]
["","SCOP/A","","","4.60","4.60","4.28"]
["Notes","","","","(1) - See separate drawing for operation range","(1) - See separate drawing for operation range","(1) - See separate drawing for electrical data"]
["","","","","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - Cooling: T2: indoor temp. 26,6°CDB, 19,4°CWB, outdoor temp. 48°CDB [Btu/hr/W]"]
["","","","","(3) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m."]
["","","","","(4) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(4) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m."]