{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":32,"n_cols":7,"rows_kept":32,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXTM-A"]
[]
[]
[]
[]
["","","","","","RXTM30A2V1B","RXTM40A2V1B"]
["Димензии","Единица","","Висина","mm","605","605"]
["","","","Ширина","mm","930","930"]
["","","","Длабочина","mm","376","376"]
["Тежина","Единица","","","kg","42","42"]
["Fan motor","Speed","Cooling","Super low","rpm","800","800"]
["","","Греење","Super low","rpm","400","400"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Operation range","Cooling","Ambient","Min.","°CDB","-10","-10"]
["","","","Max.","°CDB","46","46"]
["","Heating","Ambient","Min.","°CWB","-31","-31"]
["","","","Max.","°CWB","18","18"]
["Sound pressure level","Cooling","","Nom.","dBA","48","48"]
["","Heating","","Nom.","dBA","49.0","49.0"]
["Разладно средство","Тип","","","","R-32","R-32"]
["","Полнење","","","kg","0.97","0.97"]
["Refrigerant","Charge","","","tCO2Eq","0.66","0.66"]
["Разладно средство","GWP","","","","675.0","675.0"]
["Piping connections","Piping length","OU - IU","Max.","m","20","20"]
["","Additional refrigerant charge","","","kg/m","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)"]
["","Level difference","IU - OU","Max.","m","15.0","15.0"]
["Standard Accessories","Installation manual","","","","1","1"]
["","Refrigerant charge label","","","","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1"]
["Напојување со струја","Фаза","","","","1~","1~"]
["Power supply","Frequency","","","Hz","50","50"]
["","Voltage","","","V","220-240","220-240"]